## Calculation
Expansion Vessel Size Calculation Sheet
Calculation Date | 2015-12-23
Enter System Volume | 1000 | Litres
Enter Cold Feed Pressure | 2 | BarG
Enter Maximum Hot Pressure | 3 | BarG
Enter Cold Temperature | 10 | DegC
Enter Hot Temperature | 60 | DegC
Density of Water at Cold | 999.8 | kg/m3
Density of Water at Hot | 983.1 | kg/m3
Minimum Expansion Vessel Size | 67 | Litre
Recommended Total Capacity Size | 80 | Litre
Disclaimer: This calculation sheet and the data produced is based on calculations made by Arbe Integrated Engineering. Arbe Integrated Engineering do not accept any liability for any expansion vessel sizings made on this spreadsheet by any person who is not employed by Arbe Integrated Engineering. It should be used as guidance only

## Chart (hidden)
Expansion Vessel Size Calculation Sheet
Date: December 2015
Cold Feed Pressure (BarG) | 2 |  | 2.5 |  | 3 |  | 3.5 |  | 4 |  | 4.5 |  | 5
Max. Working Pressure (BarG) | 2.5 | 3 | 3 | 3.5 | 3.5 | 4 | 4 | 4.5 | 4.5 | 5 | 5 | 5.5 | 5.5 | 6
System Capacity (Litres) | Expansion Vessel Capacity Required (Either Singles or in Multiple Vessels)
250 | 35 | 18 | 35 | 24 | 50 | 24 | 50 | 24 | 50 | 35 | 60 | 35 | 60 | 35
500 | 60 | 35 | 80 | 50 | 80 | 50 | 100 | 50 | 100 | 60 | 150 | 60 | 150 | 60
750 | 100 | 60 | 150 | 60 | 150 | 80 | 150 | 80 | 150 | 80 | 200 | 100 | 200 | 100
1000 | 150 | 80 | 150 | 80 | 200 | 100 | 200 | 100 | 200 | 150 | 300 | 150 | 300 | 150
1250 | 150 | 100 | 200 | 100 | 200 | 150 | 300 | 150 | 300 | 150 | 300 | 150 | 300 | 150
1500 | 200 | 150 | 300 | 150 | 300 | 150 | 300 | 150 | 300 | 200 | 500 | 200 | 500 | 200
1750 | 300 | 150 | 300 | 150 | 300 | 150 | 300 | 200 | 500 | 200 | 500 | 200 | 500 | 300
2000 | 300 | 150 | 300 | 200 | 500 | 200 | 500 | 200 | 500 | 300 | 500 | 300 | 500 | 300
2500 | 300 | 200 | 500 | 200 | 500 | 300 | 500 | 300 | 500 | 300 | 750 | 300 | 750 | 300
3000 | 500 | 300 | 500 | 300 | 500 | 300 | 750 | 300 | 750 | 500 | 750 | 500 | 750 | 500
3500 | 500 | 300 | 500 | 300 | 750 | 300 | 750 | 500 | 750 | 500 | 750 | 500 | 1000 | 500
4000 | 500 | 300 | 750 | 500 | 750 | 500 | 750 | 500 | 750 | 500 | 1000 | 500 | 1000 | 500
4500 | 750 | 500 | 750 | 500 | 750 | 500 | 1000 | 500 | 1000 | 500 | 1000 | 500 | 1000 | 750
5000 | 750 | 500 | 750 | 500 | 1000 | 500 | 1000 | 500 | 1000 | 750 | 1100 | 750 | 1200 | 750
5500 | 750 | 500 | 750 | 500 | 1000 | 500 | 1000 | 750 | 1100 | 750 | 1200 | 750 | 1300 | 750
6000 | 750 | 500 | 1000 | 500 | 1000 | 750 | 1100 | 750 | 1200 | 750 | 1300 | 750 | 1500 | 750
6500 | 1000 | 500 | 1000 | 500 | 1000 | 750 | 1200 | 750 | 1300 | 750 | 1500 | 750 | 1500 | 1000
7000 | 1000 | 500 | 1000 | 750 | 1100 | 750 | 1200 | 750 | 1500 | 750 | 1500 | 1000 | 1750 | 1000
7500 | 1000 | 750 | 1100 | 750 | 1200 | 750 | 1300 | 750 | 1500 | 1000 | 1750 | 1000 | 1750 | 1000
8000 | 1000 | 750 | 1100 | 750 | 1300 | 750 | 1500 | 750 | 1500 | 1000 | 1750 | 1000 | 2000 | 1000
8500 | 1100 | 750 | 1200 | 750 | 1500 | 750 | 1500 | 1000 | 1750 | 1000 | 1750 | 1000 | 2000 | 1100
9000 | 1100 | 750 | 1300 | 750 | 1500 | 1000 | 1750 | 1000 | 1750 | 1000 | 2000 | 1000 | 2000 | 1100
9500 | 1200 | 750 | 1300 | 750 | 1500 | 1000 | 1750 | 1000 | 2000 | 1000 | 2000 | 1100 | 2250 | 1200
10000 | 1200 | 750 | 1500 | 1000 | 1750 | 1000 | 1750 | 1000 | 2000 | 1100 | 2250 | 1200 | 2250 | 1200
10500 | 1300 | 750 | 1500 | 1000 | 1750 | 1000 | 2000 | 1000 | 2000 | 1100 | 2250 | 1200 | 2500 | 1300
11000 | 1500 | 750 | 1500 | 1000 | 1750 | 1000 | 2000 | 1100 | 2250 | 1200 | 2250 | 1300 | 2500 | 1500
11500 | 1500 | 1000 | 1750 | 1000 | 2000 | 1000 | 2000 | 1100 | 2250 | 1200 | 2500 | 1300 | 2750 | 1500
12000 | 1500 | 1000 | 1750 | 1000 | 2000 | 1100 | 2250 | 1200 | 2250 | 1300 | 2500 | 1500 | 2750 | 1500
12500 | 1500 | 1000 | 1750 | 1000 | 2000 | 1100 | 2250 | 1200 | 2500 | 1300 | 2750 | 1500 | 3000 | 1500
13000 | 1750 | 1000 | 2000 | 1000 | 2000 | 1200 | 2250 | 1300 | 2500 | 1500 | 2750 | 1500 | 3000 | 1750
13500 | 1750 | 1000 | 2000 | 1100 | 2250 | 1200 | 2500 | 1300 | 2750 | 1500 | 3000 | 1500 | 3000 | 1750
14000 | 1750 | 1000 | 2000 | 1100 | 2250 | 1200 | 2500 | 1500 | 2750 | 1500 | 3000 | 1750 | 3250 | 1750
14500 | 1750 | 1000 | 2000 | 1200 | 2250 | 1300 | 2500 | 1500 | 2750 | 1500 | 3000 | 1750 | 3250 | 1750
15000 | 2000 | 1100 | 2250 | 1200 | 2500 | 1300 | 2750 | 1500 | 3000 | 1750 | 3250 | 1750 | 3500 | 2000
Disclaimer: This calculation sheet and the data produced is based on calculations made by Arbe Integrated Engineering. Arbe Integrated Engineering do not accept any liability for any expansion vessel sizings made on this spreadsheet by any person who is not employed by Arbe Integrated Engineering. It should be used as guidance only

## Data (hidden)
Expansion Vessel Calcs
Inputs |  | Expansion Factor |  | Exp Vessel Selection
|  | 0 | 999.8 | 0 | 8
system vol | 1000 | 5 | 1000 | 8.1 | 18
cold fill | 2 | 10 | 999.8 | 18.1 | 24
working | 3 | 15 | 999.2 | 24.1 | 35
Cold Temp | 10 | 20 | 998.3 | 35.1 | 50
Hot temp | 60 | 25 | 997.1 | 50.1 | 60
|  | 30 | 995.7 | 60.1 | 80
|  | 35 | 994.1 | 80.1 | 100
Expansion Vessel Volume |  | 40 | 992.3 | 100.1 | 150
Vol Ex water | 16.7033 | 45 | 990.2 | 150.1 | 200
Acc Factor | 0.25 | 50 | 998 | 200.1 | 300
Min Vessel Vol | 66.8134 | 55 | 985.7 | 300.1 | 500
|  | 60 | 983.1 | 500.1 | 750
Cold Feed Size |  | 61 | 982.58 | 750.1 | 1000
20 |  | 62 | 982.06 | 1000.1 | 1100
25 |  | 63 | 981.54 | 1100.1 | 1200
35 |  | 64 | 981.02 | 1200.1 | 1300
42 |  | 65 | 980.5 | 1300.1 | 1500
50 |  | 66 | 979.94 | 1500.1 | 1750
65 |  | 67 | 979.38 | 1750.1 | 2000
80 |  | 68 | 978.82 | 2000.1 | 2250
100 |  | 69 | 978.26 | 2250.1 | 2500
5 |  | 70 | 977.7 | 2500.1 | 2750
|  | 71 | 977.1 | 2750.1 | 3000
|  | 72 | 976.5 | 3000.1 | 3250
|  | 73 | 975.9 | 3250.1 | 3500
|  | 74 | 975.3 | 3500.1 | 3750
|  | 75 | 974.7 | 3750.1 | 4000
|  | 80 | 971.6 | 4000.1 | 4250
|  | 85 | 968.4 | 4250.1 | 4500
|  | 90 | 965.1 | 4500.1 | 4750
|  | 95 | 961.7 | 4750.1 | 5000
|  | 100 | 958.1 | 5000.1 | 5250
|  | Cold | 999.8 | 5250.1 | 5500
|  | Hot | 983.1 | 5500.1 | 5500
|  | Exp Fac | 0.016703 | Ref | 80